## Slide 1
transmission infiltration ventilation
heating
solar irradiance
‘internal’ heat
heat loss
heat gain
Digital Twins for the heating transition: Analysis methods and tools, v1
Twomes Deliverable D3

## Slide 2: Digital Twins for the heating transition: Analysis methods and tools, v1
Author: Henri ter Hofte
Publication date: 23-12-2021
Parties involved: Research group Energy Transition (Windesheim)
Chair: Jeike Wallinga
Partly based on work from the following students:
Mehmet Akol, Casper Bloemendaal, Danile Dyadko, Joery Grolleman, Tristan van Heusden, Jason Kartodimedjo, Briyan Klein, Jeroen Matser, Omar Mazher, Steven de Ronde, Roald Smits, Nathan Snippe, Wouter Vogelzang
Thanks also go to:
Dirk-Jan Medendorp (Witteveen+Bos), Janet van de Wetering (Witteveen+Bos), Stephan Peters (Windesheim), Hossein Rahmani (Windesheim)
Twomes Deliverable D3
This work is financially supported by BDR Thermea, Breman, Enpuls, TechForFuture, Witteveen + Bos and the municipality of Zwolle.
This is a publication by Saxion, University of Twente and Windesheim University of Applied Sciences
Licence: CC BY 4.0, Research group Energy Transition, Windesheim University of Applied Sciences
Notes: The results of project Twomes are described in the following deliverables:
Deliverable D1a Project Plan contains the project plan that forms the basis for research activities.
Deliverable D1b Data management plan describes what data is collected in the project, how data should be handled during the project and after the project is finished.
Deliverable D1c: Uitkomsten bewonersonderzoek describes (in Dutch) the results of the research we conducted into questions residents have about the heat transition, via surveys and/or interviews. We used insights gained to focus further research in the project lays the foundation for advice modules.
Deliverable D2: Dataset 1 contains the monitoring data that we collected for exploratory analysis.
Deliverable D3: Analysis Methods and Tools, Version 1 contains a description of the analysis methods and tools used to analyze data from Deliverable D2. We also describe what we can learn from the available data and what additional measurements we deem necessary.
Deliverable D4: Testable Hypotheses describes the hypotheses we want to test with the research in Twomes.
Deliverable D5: Measurement methods and techniques describes the (additional) measurement methods and techniques that we have developed to collect data used to test hypotheses from D4.
Deliverable D6: Subject Information, Consent Forms includes all information and documents (in Dutch) we use to recruit and educate subjects, including a description of how we obtain consent to collect data.
Deliverable D7: Dataset 2 contains the data that we collected to do a detailed analysis including research into the hypotheses of D4.
Deliverable D8: Analysis Methods and Tools describes not only the analysis methods and tools we applied to the dataset from D7, but also the results and conclusions of this analysis.
Deliverable D9: Dissemination and design follow-up research includes all external presentations and publications for interested parties outside the project, including a plan for a follow-up study for the realization of advice modules.
Deliverable D10: Presentations, Report, Update Plan and Schedule includes all interim and progress presentations of the project, and updated plans.

## Slide 3: Some interventions to reduce home heating CO2-emissions
Building interventions isolation, crack sealing, HR++ glass, …
Installation interventions
  Installation: hardware high efficiency boiler, heat recovery, (hybrid) heat pump, district heating, biogas, biomass, hydrogen, infrared,…
  Installation: settings night setback, day setback, hydronic balancing, supply temperature, …
Comfort interventions warm clothing?, get used to lower temperatures?, …
Weather climate change?
Introduction
Notes: Since space in diagrams is limited; I switched to collapsing instatataion hardware interventions and installation settings interventions into one category. In subsequent slides, this allows for model parameter categories to be collapsed in to ‘installation parameters’.
Installation settings, however are often much easier to change than installation hardware. For example, changing the supply temperature of a gas-fired boiler is much easier than changing the gas-fired boiler for a heat pump (which often also implies changing the hydronic heat distribution system and sometimes even requires changing heat distribution of the the building envelope.

## Slide 4: hich model parameters for the home heating transition of specific residential buildings can we learn from energy monitoring data in order to answer household questions for their home heating transition?

## Slide 5: Modeling home heating
time series output data
WP3 Data Analysis & Prediction
indoor temperature
energy use
setpoint changes
weather
building
installation
comfort needs
time series input data

## Slide 6: Modeling home heating
WP3 Data Analysis & Prediction
indoor temperature
energy use
setpoint changes
weather
time series output data
time series input data
building
installation
comf.needs
model parameters (time-independent)

## Slide 7: Building model overview
WP3 Data Analysis & Prediction
transmission infiltration ventilation
heating system (boiler + distribution)
solar irradiance
‘internal’ heat
…of occupants, (electric) devices, and hot water
effective heat demand ΔSeff;t [K s] specific heat loss H [W/K]
where
ΔSeff;t = Σ((Tin;t-Tout;eff;t) Δt)
heat los
heat gain
Σ( Δt) [J/m2] Aeff [m2] where It = average global horizontal irradiance from time t to Δt [W/m2]
Gas for heating ΔGCH [Nm3] superior calorific value natural gas
upper net heating system efficiency ηhs;CH [%]
Notes: Model paramters are formatted in green
Time series data is has a subscript t; e.g. Tin;t is Tin (the average indoor temperature) at time interval t. Time intervals last a duration Δt.
N.B. This is the most simple building model; the effect of wind (a factor in infiltration) and changes in ventilation behaviour are modelled via effective outdoor temperature (Tout;eff;t), where accurding to KNMI research, the best simple approsimation is Tout;eff;t [°C] = Tout;eff;t – 2/3* ut [m/s], where ut is the average wind speed during time interval t. In more refines models, we will try to separate the influence of wind on the home heat los as a separate model parameter that is to be learned.

## Slide 8: Model parameters we would like to learn, that determine time series output (indoor temperature, energy use), depending on time series input data
Buiding specific heat loss H [W/K], thermal inertia  [h] ~ thermal mass C [J/K], effective solar aperture Aeff [m2]
Installation
  Hardware efficiency  [%], heating power Peff [W]
  Settings maximal supply temperature Tsup [°C], hydronic balancing valve settings, thermostat program Tprog;t_start;t_end [°C], temporary setpoint changes Tset [°C]
Comfort needs comfort temperature(s) while home Tset;home [°C] / Tset;sleep [°C]
Weather outdoor temperature Tout [°C], wind U [m/s], solar global horizontal irratiance I [W/m2]
WP3 Data Analysis & Prediction
Effective heat demand [K·s]

## Slide 9: Inverse grey-box modelling of home heating
calculated data (time series data)
calculated output data (time series data)
WP3 Data Analysis & Prediction
indoor temperature
energy use
setpoint changes
weather
calculated data (time series data)
measured input data (time series data)
building
installation
comf.needs
model parameters (time-independent)
indoor temperature
energy use
measured comparison data (time series data)
?
calculated data (time series data)
calculated data (time series data)
calculated data (time series data)
calculated data (time series data)
calculated data (time series data)
calculated data (time series data)
calculated data (time series data)
calculated data (time series data)
calculated data (time series data)
calculated data (time series data)

## Slide 10: Why ‘inverse’ modelling and what is a ‘digital twin’?
Normal (forward) modelling
  IN: time series data + model parameters
  OUT: calculated time series data & performance metrics
Inverse modelling
  IN: time series data + measured time series data & performance metrics
  OUT: model parameters
A model with well learnt parameters is called a ‘digital twin’
WP3 Data Analysis & Prediction

## Slide 11: Model parameters: time-independent characteristics that determine home heating performance
Building model parameters
Installation model parameters
  Installation hardware model parameters
  Installation settings model parameters
Comfort needs model parameters
WP3 Data Analysis & Prediction

## Slide 12: Predict how changed parameters change outcome
WP3 Data Analysis & Prediction
indoor temperature
energy use
setpoint changes
weather
calculated data
time series data
building
installation
comf.needs
model parameters (time-independent)
Notes: Thermostat setpoints can be e.g. replayed from a previous year, or derived from comfort needs. This depends on the type of prediction and comparison desired. Similarly, weather data can be e.g. replayed from a prvious year, or derived from a pre-determind average, also known as a ‘reference climate year’. Again, this depends on the type of prediction and comparison desired.

## Slide 13: Data we intend to measure
category | measured data
comfort desires | setpoint
weather | outdoor temperature
 | wind
 | solar irradiation
indoor | indoor temperature
installation | supply temperature
 | return temperature
 | burn mode
energy use | electricity usage
 | gas usage
building | address, floor area, type
WP2 Data Acquisition, Privacy & Open Data
Notes: Other words used in the Twomes project for ‘data observation’ in the project are also ‘data monitoring’ (in ‘energy data monitoring’) and ‘acquire’ (in ‘WP2 Data acquisition’).

## Slide 14: Data we intend to measure
category | measured data | symbol | unit | connect? (API) | OpenTherm (ID) | sensor
comfort desires | setpoint | Tset | °C | ? | (16) | 
weather | outdoor temperature | Tout | °C | (KNMI) |  | 
 | wind | W | m/s |  |  | 
 | global horizontal irradiance | I | W/m2 |  |  | 
indoor | indoor temperature | Tin | °C |  | (24) | 
installation | supply temperature | Tsup | °C |  | (25) | 
 | return temperature | Tret | °C |  | (28) | 
 | burn mode | CH/DHW |  |  | (0) | 
energy use | electricity usage | E | kWh |  P3/P4 (Enelogic) | P1 | 
 | gas usage | G | m3 |  |  | 
building | address, floor area, type |  |  | ? (BAG) |  | 
WP2 Data Acquisition, Privacy & Open Data

## Slide 15: Model parameters we seek to learn
symbol | scope | parameter | unit
H | building | specific heat loss | W/K
 | building | thermal inertia | h
Ceff | building | effective thermal mass (Ceff = H  τ  60 60) | J/K
Aeff | building | effective horizontal area of the solar aperture | m2
Pmax | installation | maximum heating system power (boiler+distribution) | W
ηupper;CH | installation | upper central heating system efficiency | %
COP | installation | coefficient of performance | -
<Tset;h;d> | comfort needs | thermostat program (setpoints per hour per day) | °C
WP3 Data Analysis & Prediction

## Slide 16: Color coding legend
model parameters (green)
  case-specific, constant in the time horizon considered
measured input data (pink)
  case-specific, varying in the time horizon considered
fixed model parameters (blue)
  population averages, constant in the time horizon considered
WP3 Data Analysis & Prediction

## Slide 17: Building model equations
, the temperature rise from time t to time t+Δt
, the heat loss from time t to time t+Δt
is the specific heat loss, a building model parameter
, the effective temperature difference at time t
, the indoor temperature at time t, measured via an indoor temperature sensor
, the effective outdoor temperature at time t
, the geospatially interpolated outdoor temperature at time t, calculated from measured wheather data from the KNMI API
, the geospatially interpolated wind speed at time t, calculated from measured wheather data from the KNMI API
(see next slide)
, the effective thermal inertia, a building model parameter
, the effective heat capacity of the home, a building model parameter derived from two others
WP3 Data Analysis & Prediction
Notes: Effective outdoor temperature calculation correction factor is derived from N Wever. Effectieve temperatuur en graaddagen, klimatologie en klimaatscenario\'s KNMI number: PUBL-219, Year: 2008. https://cdn.knmi.nl/knmi/pdf/bibliotheek/knmipubmetnummer/knmipub219.pdf

## Slide 18: Building model equations (2)
t
, a model parameter
, the natural gas used for central heating
, the natural gas supplied to the home, measured via smart meter readings
, the geospatially interpolated global horizontal irradiation at time t, calculated from measured wheather data from the KNMI API
WP3 Data Analysis & Prediction
Notes: I need to figure out what we really measure here: [Nm^3], or [Geq].
"- Normaal m3 (Nm3): Idem bij een druk van 101,325 kPa (of 1,01325 bar) en 0 °C. Deze kubieke meter wordt als Normaal m3 omschreven in norm met nummer 5024-1976(E) van de Internationale Organisatie voor Standaardisatie (ISO);
- Gronings-aardgasequivalent (Geq): Om te kunnen rekenen met volumes aardgas van verschillende kwaliteit worden deze herleid tot een Gronings-aardgasequivalent. Op basis van het verschil in verbrandingswarmte van de diverse gaskwaliteiten wordt deze omgerekend tot een (fictief) volume van Groningen kwaliteit (dat is 35,17 megajoule (MJ) per m3 van 0 °C en 101,325 kPa, of 1,01325 bar). Bijvoorbeeld: Eén Nm3 gas met een verbrandingswaarde van 36,5 MJ is 36,5/35,17 is 1,0378 Nm3 Geq."
Source: https://nl.wikipedia.org/wiki/Aardgaswinning_in_Nederland
De DSMR5 standaard voor de slimme meter schrijft voor dat de P1 poort elke seconde de laatst ontvangen 5-minuten waarde & timestamp doorgeeft|: "Last 5-minute value (temperature
converted), gas delivered to client in m3, including decimal values and capture time"
Deze waarde is dus temperatuurgecorrigeerd, dus Nm^3; het is niet gecorrigeerd voor calorische samenstelling.
Als het nodig is kunnen we de Geq berekenen via data die hier beschikbaar is; https://www.gasunietransportservices.nl/aangeslotenen/gaskwaliteit-en-meetzaken/calorische-waarden

## Slide 19: Building model equations (3)
, measured via smart meter redings
(see Building Model Equations slide 3)
(see Building Model Equations slide 4)
WP3 Data Analysis & Prediction

## Slide 20: Building model equations (4)
, the average metabolic rate of the activities of person p
, an estimate of the body surface area of person p.
, the number of persons in the home
WP3 Data Analysis & Prediction
Notes: Uit: Kooger, Ter Hofte, Dreijerink, Tigchelaar, De Smidt, Peddemors (2019), Bevindingen haalbaarheidsonderzoek VeniVidiFlexi. Onderzoek naar energiebesparing bij huishoudens door slim verwarmen tijdens afwezigheid, TNO, Available online: Bevindingen haalbaarheidsonderzoek VeniVidiFlexi. Onderzoek naar energiebesparin :: TNO Repository (tudelft.nl)
Voor het bepalen van de nuttige restwarmte van personen, Qrest;pp, gebruiken we een daggemiddelde waarde van 5,29 MJ per dag (gemiddeld 61 W op per bewoner). Hierbij hebben we een gemiddelde verondersteld van 8,6 uur per dag slapen met restwarmtevermogen van 77 W, 7,7 uur per dag aanwezigheid met gemiddeld restwarmtevermogen van 105 W en 7,7 uur per dag afwezigheid, met een gemiddeld restwarmtevermogen van 0 W.
De wattages per vierkante meter huidoppervlak uit Tabel B.3 van (ISO, 2004) en het huidoppervlak met de formule van (DuBois & DuBois, 1916), geciteerd in (Nicol, Humphreys, & Roaf, 2012):
Hierbij hebben we voor het gemiddelde gewicht 77,5 kg gebruikt en voor de gemiddelde lengte van 1,741 cm, overeenkomstig de gemiddelde waarden van inwoners van Nederland van 20 jaar (Centraal Bureau voor de Statistiek, 2019).
De gemiddelde tijdsduren voor slapen, aanwezigheid en afwezigheid hebben we daarbij niet afgeleid van de data van de Drebbl app, maar van (Sociaal en Cultureel Planbureau, 2019). De berekening van de energiebesparing door beter aan te sluiten op aanwezigheidspatronen is niet erg gevoelig voor de restwarmte die aanwezige personen opleveren.
Uit: Kooger, Ter Hofte, Dreijerink, Tigchelaar, De Smidt, Peddemors (2019), Bevindingen haalbaarheidsonderzoek VeniVidiFlexi. Onderzoek naar energiebesparing bij huishoudens door slim verwarmen tijdens afwezigheid, TNO, Available online: Bevindingen haalbaarheidsonderzoek VeniVidiFlexi. Onderzoek naar energiebesparin :: TNO Repository (tudelft.nl)
Voor het bepalen van de nuttige restwarmte van personen, Qrest;pp, gebruiken we een daggemiddelde waarde van 5,29 MJ per dag (gemiddeld 61 W op per bewoner). Hierbij hebben we een gemiddelde verondersteld van 8,6 uur per dag slapen met restwarmtevermogen van 77 W, 7,7 uur per dag aanwezigheid met gemiddeld restwarmtevermogen van 105 W en 7,7 uur per dag afwezigheid, met een gemiddeld restwarmtevermogen van 0 W.
De wattages per vierkante meter huidoppervlak uit Tabel B.3 van (ISO, 2004) en het huidoppervlak met de formule van (DuBois & DuBois, 1916), geciteerd in (Nicol, Humphreys, & Roaf, 2012):
𝑏𝑜𝑑𝑦 𝑠𝑢𝑟𝑓𝑎𝑐𝑒 𝑎𝑟𝑒𝑎 [𝑚^2 ]=〖0,202× 𝑤𝑒𝑖𝑔ℎ𝑡 [𝑘𝑔]〗^0,425×〖𝑙𝑒𝑛𝑔𝑡ℎ [𝑚]〗^0,725
Hierbij hebben we voor het gemiddelde gewicht 77,5 kg gebruikt en voor de gemiddelde lengte van 1,741 cm, overeenkomstig de gemiddelde waarden van inwoners van Nederland van 20 jaar (Centraal Bureau voor de Statistiek, 2019).
De gemiddelde tijdsduren voor slapen, aanwezigheid en afwezigheid hebben we daarbij niet afgeleid van de data van de Drebbl app, maar van (Sociaal en Cultureel Planbureau, 2019). De berekening van de energiebesparing door beter aan te sluiten op aanwezigheidspatronen is niet erg gevoelig voor de restwarmte die aanwezige personen opleveren.

## Slide 21: Estimating internal heat contribution from occupants
, the average metabolic rate for a person sleeping
, the average metabolic rate for a person at rest and sitting
, the average daily sleeping duration of inhabitabts in the Netherlands
, the average daily duration of presence (we assume: at rest and sitting) of inhabitabts at home in the Netherlands
, the number of persons in the household living in the home, measured via a questionnaire and/or the Twomes app
From these estimates, we derive te following estimate for the internal heat gain from persons from time t to t+Δt (see also next slide):
WP3 Data Analysis & Prediction
Notes: Uit: Kooger, Ter Hofte, Dreijerink, Tigchelaar, De Smidt, Peddemors (2019), Bevindingen haalbaarheidsonderzoek VeniVidiFlexi. Onderzoek naar energiebesparing bij huishoudens door slim verwarmen tijdens afwezigheid, TNO, Available online: Bevindingen haalbaarheidsonderzoek VeniVidiFlexi. Onderzoek naar energiebesparin :: TNO Repository (tudelft.nl)
Voor het bepalen van de nuttige restwarmte van personen, Qrest;pp, gebruiken we een daggemiddelde waarde van 5,29 MJ per dag (gemiddeld 61 W op per bewoner). Hierbij hebben we een gemiddelde verondersteld van 8,6 uur per dag slapen met restwarmtevermogen van 77 W, 7,7 uur per dag aanwezigheid met gemiddeld restwarmtevermogen van 105 W en 7,7 uur per dag afwezigheid, met een gemiddeld restwarmtevermogen van 0 W.
De wattages per vierkante meter huidoppervlak uit Tabel B.3 van (ISO, 2004) en het huidoppervlak met de formule van (DuBois & DuBois, 1916), geciteerd in (Nicol, Humphreys, & Roaf, 2012):
Hierbij hebben we voor het gemiddelde gewicht 77,5 kg gebruikt en voor de gemiddelde lengte van 1,741 cm, overeenkomstig de gemiddelde waarden van inwoners van Nederland van 20 jaar (Centraal Bureau voor de Statistiek, 2019).
De gemiddelde tijdsduren voor slapen, aanwezigheid en afwezigheid hebben we daarbij niet afgeleid van de data van de Drebbl app, maar van (Sociaal en Cultureel Planbureau, 2019). De berekening van de energiebesparing door beter aan te sluiten op aanwezigheidspatronen is niet erg gevoelig voor de restwarmte die aanwezige personen opleveren.
Uit: Kooger, Ter Hofte, Dreijerink, Tigchelaar, De Smidt, Peddemors (2019), Bevindingen haalbaarheidsonderzoek VeniVidiFlexi. Onderzoek naar energiebesparing bij huishoudens door slim verwarmen tijdens afwezigheid, TNO, Available online: Bevindingen haalbaarheidsonderzoek VeniVidiFlexi. Onderzoek naar energiebesparin :: TNO Repository (tudelft.nl)
Voor het bepalen van de nuttige restwarmte van personen, Qrest;pp, gebruiken we een daggemiddelde waarde van 5,29 MJ per dag (gemiddeld 61 W op per bewoner). Hierbij hebben we een gemiddelde verondersteld van 8,6 uur per dag slapen met restwarmtevermogen van 77 W, 7,7 uur per dag aanwezigheid met gemiddeld restwarmtevermogen van 105 W en 7,7 uur per dag afwezigheid, met een gemiddeld restwarmtevermogen van 0 W.
De wattages per vierkante meter huidoppervlak uit Tabel B.3 van (ISO, 2004) en het huidoppervlak met de formule van (DuBois & DuBois, 1916), geciteerd in (Nicol, Humphreys, & Roaf, 2012):
𝑏𝑜𝑑𝑦 𝑠𝑢𝑟𝑓𝑎𝑐𝑒 𝑎𝑟𝑒𝑎 [𝑚^2 ]=〖0,202× 𝑤𝑒𝑖𝑔ℎ𝑡 [𝑘𝑔]〗^0,425×〖𝑙𝑒𝑛𝑔𝑡ℎ [𝑚]〗^0,725
Hierbij hebben we voor het gemiddelde gewicht 77,5 kg gebruikt en voor de gemiddelde lengte van 1,741 cm, overeenkomstig de gemiddelde waarden van inwoners van Nederland van 20 jaar (Centraal Bureau voor de Statistiek, 2019).
De gemiddelde tijdsduren voor slapen, aanwezigheid en afwezigheid hebben we daarbij niet afgeleid van de data van de Drebbl app, maar van (Sociaal en Cultureel Planbureau, 2019). De berekening van de energiebesparing door beter aan te sluiten op aanwezigheidspatronen is niet erg gevoelig voor de restwarmte die aanwezige personen opleveren.

## Slide 22: Average contribution to home heating of heat dissipated by average household member
Occupancy | Activity3) | Metabolic rate3) [W/m2] | Height1) [m] | Weight1) [kg] | Abody2) [m2] | Power [W] | Duration4) [h] | Heat [MJ/d]
present | sleeping | 40 | 1,74 | 77,5 | 1,92 | 77 | 8,6 | 2,38
present | at rest, sitting | 55 | 1,74 | 77,5 | 1,92 | 105 | 7,7 | 2,92
absent |  | 0 | 1,74 | 77,5 | 1,92 | 0 | 7,7 | 0,00
TOTAL |  |  |  |  |  | 61 | 24,0 | 5,29
WP3 Data Analysis & Prediction
Sources: 1) Centraal Bureau voor de Statistiek. (2019). Lengte en gewicht van personen, ondergewicht en overgewicht; vanaf 1981. Opgehaald van StatLine: https://statline.cbs.nl/Statweb/publication/?DM=SLNL&PA=81565NED&D1=5-6&D2=0&D3=5&D4=0&D5=l&HDR=G1,T&STB=G2,G3,G4&VW=T
2) DuBois, D., & DuBois, E. (1916). A formula to estimate the approximate surface area if height and weight be known. Arch Intern Medicine, 17, 863-871.
3) ISO. (2004). Ergonomics of the thermal environment - Determination of metabolic rate (ISO 8996:2004). ISO.
4) Sociaal en Cultureel Planbureau. (2019). Tijdsbestedingsonderzoek (TBO). Opgehaald van https://www.scp.nl/Onderzoek/Bronnen/Beknopte_onderzoeksbeschrijvingen/Tijdsbestedingsonderzoek_TBO
Notes: Uit: Kooger, Ter Hofte, Dreijerink, Tigchelaar, De Smidt, Peddemors (2019), Bevindingen haalbaarheidsonderzoek VeniVidiFlexi. Onderzoek naar energiebesparing bij huishoudens door slim verwarmen tijdens afwezigheid, TNO, Available online: Bevindingen haalbaarheidsonderzoek VeniVidiFlexi. Onderzoek naar energiebesparin :: TNO Repository (tudelft.nl)
Voor het bepalen van de nuttige restwarmte van personen, Qrest;pp, gebruiken we een daggemiddelde waarde van 5,29 MJ per dag (gemiddeld 61 W op per bewoner). Hierbij hebben we een gemiddelde verondersteld van 8,6 uur per dag slapen met restwarmtevermogen van 77 W, 7,7 uur per dag aanwezigheid met gemiddeld restwarmtevermogen van 105 W en 7,7 uur per dag afwezigheid, met een gemiddeld restwarmtevermogen van 0 W.
De wattages per vierkante meter huidoppervlak uit Tabel B.3 van (ISO, 2004) en het huidoppervlak met de formule van (DuBois & DuBois, 1916), geciteerd in (Nicol, Humphreys, & Roaf, 2012):
Hierbij hebben we voor het gemiddelde gewicht 77,5 kg gebruikt en voor de gemiddelde lengte van 1,741 cm, overeenkomstig de gemiddelde waarden van inwoners van Nederland van 20 jaar (Centraal Bureau voor de Statistiek, 2019).
De gemiddelde tijdsduren voor slapen, aanwezigheid en afwezigheid hebben we daarbij niet afgeleid van de data van de Drebbl app, maar van (Sociaal en Cultureel Planbureau, 2019). De berekening van de energiebesparing door beter aan te sluiten op aanwezigheidspatronen is niet erg gevoelig voor de restwarmte die aanwezige personen opleveren.
Uit: Kooger, Ter Hofte, Dreijerink, Tigchelaar, De Smidt, Peddemors (2019), Bevindingen haalbaarheidsonderzoek VeniVidiFlexi. Onderzoek naar energiebesparing bij huishoudens door slim verwarmen tijdens afwezigheid, TNO, Available online: Bevindingen haalbaarheidsonderzoek VeniVidiFlexi. Onderzoek naar energiebesparin :: TNO Repository (tudelft.nl)
Voor het bepalen van de nuttige restwarmte van personen, Qrest;pp, gebruiken we een daggemiddelde waarde van 5,29 MJ per dag (gemiddeld 61 W op per bewoner). Hierbij hebben we een gemiddelde verondersteld van 8,6 uur per dag slapen met restwarmtevermogen van 77 W, 7,7 uur per dag aanwezigheid met gemiddeld restwarmtevermogen van 105 W en 7,7 uur per dag afwezigheid, met een gemiddeld restwarmtevermogen van 0 W.
De wattages per vierkante meter huidoppervlak uit Tabel B.3 van (ISO, 2004) en het huidoppervlak met de formule van (DuBois & DuBois, 1916), geciteerd in (Nicol, Humphreys, & Roaf, 2012):
𝑏𝑜𝑑𝑦 𝑠𝑢𝑟𝑓𝑎𝑐𝑒 𝑎𝑟𝑒𝑎 [𝑚^2 ]=〖0,202× 𝑤𝑒𝑖𝑔ℎ𝑡 [𝑘𝑔]〗^0,425×〖𝑙𝑒𝑛𝑔𝑡ℎ [𝑚]〗^0,725
Hierbij hebben we voor het gemiddelde gewicht 77,5 kg gebruikt en voor de gemiddelde lengte van 1,741 cm, overeenkomstig de gemiddelde waarden van inwoners van Nederland van 20 jaar (Centraal Bureau voor de Statistiek, 2019).
De gemiddelde tijdsduren voor slapen, aanwezigheid en afwezigheid hebben we daarbij niet afgeleid van de data van de Drebbl app, maar van (Sociaal en Cultureel Planbureau, 2019). De berekening van de energiebesparing door beter aan te sluiten op aanwezigheidspatronen is niet erg gevoelig voor de restwarmte die aanwezige personen opleveren.

## Slide 23: Building model equations (5)
, but for other purposes
, an installation model parameter
WP3 Data Analysis & Prediction

## Slide 24: Estimating internal heat contribution from gas used not for central heating (1)
our estimate for the upper heating efficiency of turning natural gas into heat when gas is used for other proposed than central heating (see also next slide)
WP3 Data Analysis & Prediction

## Slide 25: Estimating internal heat contribution from gas used not for central heating (2)
Symbol | Application | Average gas use [Nm3/y] | Average superior calorific efficiency [%] | Heat fraction remaining in home [%] | Effective upper home heating efficiency [%] | Average heat [W]
Qint;cook | cooking | 39 | 44,4 % | 46% | 20,4 % | 9
Qint;DHW | Domestic Hot Water | 300 | 71,6 % | 50% | 35,8 % | 120
Qint;noCH | cooking and DHW | 339 |  |  | 34,0 % | 129
WP3 Data Analysis & Prediction
Notes: Uit: Kooger, Ter Hofte, Dreijerink, Tigchelaar, De Smidt, Peddemors (2019), Bevindingen haalbaarheidsonderzoek VeniVidiFlexi. Onderzoek naar energiebesparing bij huishoudens door slim verwarmen tijdens afwezigheid, TNO, Available online: Bevindingen haalbaarheidsonderzoek VeniVidiFlexi. Onderzoek naar energiebesparin :: TNO Repository (tudelft.nl)
N.B. to get from [NM^3/y] via efficiency and remaining heat to average heat in value, multiply by superior calorific value of 35.170.000 J/NM^3 and divide by (365,25[d/y]*24[h/d]*60[min/h]*60[s/min]) Het gasverbruik voor koken en warm tapwaterbereiding, Gkoken+ww, is niet af te lezen uit de intervalstanden van de slimme meter, daaruit kan alleen het totale gasverbruik worden afgeleid. We leiden Gdag;koken+ww, het gemiddelde dagverbruik voor koken en warm tapwater, af uit het verbruik buiten het stookseizoen, waarbij we de dagen en het verbruik tijdens de dagen dat er niemand afwezig is (bijvoorbeeld tijdens een zomervakantie), uitsluiten van de berekening.
Elke toepassing van aardgas heeft daarbij een eigen efficiëntie voor het opwekken van warmte. Uit onze gevoeligheidsanalyse (zie ook A.9) bleek dat de relatieve besparing op ruimteverwarming door stookonderbrekingen niet bijzonder gevoelig is voor de efficiëntie waarmee gas wordt omgezet in warmte (dit in tegenstelling tot de gevoeligheid van het absolute energiegebruik, dat natuurlijk wel gevoelig is voor de efficiëntie waarmee gas wordt omgezet in warmte!). Daarom volstaan we in de berekeningen van de nuttige restwarmte die gasverbruik voor koken en warm tapwater met een landelijk gemiddelde voor het nuttig rendement van restwarmte uit koken en warm tapwater, namelijk 34 %, zoals berekend in Tabel 1.

## Slide 26: Estimating internal heat contribution from gas used not for central heating (3)
, but for other purposes
, the average gas usage speed for other purposes than central heating Alternative simpler model: = 339/(365*24*60*60) [Nm3/s]
, the total gas usage during the months May - August, measured via a smart meter N.B. Via the P3/P4 interface, monthly interval measurements are available starting 13 months in the past
, the duration of the months May – August
WP3 Data Analysis & Prediction

## Slide 27: Estimating internal heat contribution from electricity used for central heating
is the electricity used by a heat pump to heat the home from time t to time t+Δt, measured via a dedicated kWh meter
the coefficient of performance of the heat pump
, t
WP3 Data Analysis & Prediction

## Slide 28: 0. Geospatial interpolation of weather data
Observations needed
  8, 9, 22, measured from KNMI API, but not yet geospatially interpolated
Model equations
Calculation of geospatial interpolation
  Analytic: linear regression
  Curve-fitting
    iterate over space, not over time!
Initial Analysis Strategy

## Slide 29: 1a. Calculate thermal inertia τeff [s] from 0-4 AM
Data (observations) needed
  (6) , the indoor temperature at time t, measured via an indoor temperature sensor
  (8) , is the geospatially interpolated outdoor temperature at time t, calculated from measured wheather data from the KNMI API
  , is the geospatially interpolated wind speed at time t, calculated from measured wheather data from the KNMI API
  (22) , is the geospatially interpolated global horizontal irradiation at time t, calculated from measured wheather data from the KNMI API
Filter data (first simple filter; based on local time)
  Remove intervals with timestamps between 04:00 and 00:00 local time (NB timestamps are in UTC, convert to local time first),
Calculation
  (7) , is the effective outdoor temperature at time t
  (5) , the effective temperature difference at time t
  τeff of each filtered contiguous period as:
  duration-weighted average of τeff of all filtered contiguous periods
Initial Analysis Strategy

## Slide 30: 1b. Calculate thermal inertia τeff [s] filtered better
Data (observations) needed
  (6) , is the indoor temperature at time t, measured via an indoor temperature sensor
  (8) , is the geospatially interpolated outdoor temperature at time t, calculated from measured wheather data from the KNMI API
  , is the geospatially interpolated wind speed at time t, calculated from measured wheather data from the KNMI API
  (22) , is the geospatially interpolated global horizontal irradiation at time t, calculated from measured wheather data from the KNMI API
  (18) is the natural gas supplied to the home via the natural gas net from time t to time t+Δt, measured via a smart meter
  (66) is the electricity used by a heat pump to heat the home from time t to time t+Δt, measured via a dedicated kWh meter
Filter data (second, more realistic filter)
  Remove intervals with heat gains, i.e. or or
  Remove non-contiguous periods with a duration
  Remove contiguous periods where
Calculation
  (7) , is the effective outdoor temperature at time t
  (5) , the effective temperature difference at time t
  τeff of each filtered contiguous period as:
  duration-weighted average of τeff of all filtered contiguous periods
Initial Analysis Strategy

## Slide 31: 1c. Curve-fit thermal inertia τeff [s] on filtered periods
Data (observations) needed: see previous slide
Filter data similar to analysis 1b (see previous slide)
Model equations
  (13) is zero (a deliberate simplification for )!
  Hence, combining (1,2,4,5,7, 12), we get , the temperature rise from time t to time t+Δt
Try two simulation intervals: Δt = 15 min and Δt = 5 min
Make sure the python curve fitting library minimizes for each filtered contiguous period:
  Root Mean Squared Error (RMSE) of Tin (between the the measured and simulated indoor temperature):
Finally,
  plot a duration-weighted histogram for all τeff calculated for all filtered contiguous periods of each building (weighted on duration of contiguous period of τeff )
  calculate a duration-weighted average for τeff calculated for all filtered contiguous periods of each building (weighted on duration of contiguous period of τeff )
Initial Analysis Strategy

## Slide 32: 2. Calculate the volumetric boiler efficiency Qvol;CH [J/Nm3] based on Tret and generic efficiency lookup table
Data needed
  (64) , the temperature returning to the boiler from the radiators between time t1 and t2, measured via an OpenTherm monitor or a temperature sensor on the return feed
  (65) , a boolean value that determines whether the boiler has ONLY been burning gas for central heating between time t1 and t2 (), or not () measured via an OpenTherm monitor
  Generic formula/table derived with WebPlotDigitizer app from graph in this report that associates Tret [] with the inferior efficiency, ηhi;CH [%]
    if
    if
Procedure
  Do not consider (i.e. filter away periods) where , consider only data for periods where
  Based in Tret [] look up the inferior efficiency, ηhi;CH[%] of each interval and note the duration
  Calculate the duration-weighted average for ηhi;CH [%]
Output
  , the inferior heating efficiency of the boiler when heating the home using natural gas
  d
Initial Analysis Strategy
Notes: Natural gas from the Groningen field has a lower heating value of 31,65 [MJ/Nm^3] and an superior calorific value of 35,17 [MJ/Nm^3] (source: https://nl.wikipedia.org/wiki/Verbrandingswarmte)
The superior calorific value includes the potential energy you can fully harvest latent heat present in the exhaust gasses, by letting these condensate within the boiler.
The efficiency percentages you encounter in systems burning natural gas be expresses as upper heating value efficiency of low heating value efficiency. To avoid confusion, make sure you output all metrics below:
When using Groningen natural gas, either calculate:
volumetric efficiency [J/Nm^3] == 31,65 [MJ/Nm^3]  1.000.000 [J/MJ]  lower heating efficiency [%].
volumetric efficiency [J/Nm^3] == 35,17 [MJ/Nm^3]  1.000.000 [J/MJ]  upper heating efficiency [%].

## Slide 33: 3. Curve-fit H [W/K] & Aeff [m2]
Data needed:
  (6), measured via an indoor temperature sensor
  (15)
  (8), (9), (22), measured from KNMI API (and then geospatially interpolated)
  (18), (27), (28), measured via P1 port of P3/P4 port data of the smart meter
  (62), measured via P1 port of P3/P4 port data of the smart meter
  (29), measured via a PV-yield meter
  (30), assumed to be zero for the Berkum energy pilot
  (45), measured via Henri via administration of deltaWonen (assume Np = 2,2 as long as unknown)
Simulation model: equation 1 and precedents
Minimize: Root Mean Squared Error of Tin, the measured and simulated indoor temperature:
Initial Analysis Strategy

## Slide 34: ?. Calculate boiler efficiency ηupper;CH [%] based on return temperature and specific lookup table
Data needed
  , the temperature returning to the boiler from the radiators at time t, measured via an OpenTherm monitor or a temperature sensor on the return feed
  Brand and model of the heating boiler, measured via the survey questionnaire
  Brand and model-specific graph/table that associates Tret with ηupper;CH [%]
Procedure
  Similar to procedure when using generic efficiency lookup table
Output
  Lower heating efficiency of the boiler [%]
  Upper heating efficiency of the boiler [%]
  Volumetric efficiency of the boiler [J/Nm^3]
Initial Analysis Strategy
Notes: Natural gas from the Groningen field has a lower heating value of 31,65 [MJ/Nm^3] and a superior calorific value of 35,17 [MJ/Nm^3] (source: https://nl.wikipedia.org/wiki/Verbrandingswarmte)
The upper heating value includes the potential energy you can fully harvest latent heat present in the exhaust gasses, by letting these condensate within the boiler.
The efficiency percentages you encounter in systems burning natural gas be expresses as upper heating value efficiency of low heating value efficiency. To avoid confusion, make sure you output all metrics below:
When using Groningen natural gas, either calculate:
volumetric efficiency [J/Nm^3] == 31,65 [MJ/Nm^3]  1.000.000 [J/MJ]  lower heating efficiency [%].
volumetric efficiency [J/Nm^3] == 35,17 [MJ/Nm^3]  1.000.000 [J/MJ]  upper heating efficiency [%].

## Slide 35: ?. Calculate boiler efficiency ηupper;CH [%] based on supply temperature and return temperature
Data needed
  , the temperature returning to the boiler from the radiators at time t, measured via an OpenTherm monitor or a temperature sensor on the return feed
  , the temperature supplied from the boiler to the radiators at time t, measured via an OpenTherm monitor or a temperature sensor on the return feed
  , the volumetric flow rate of the water fowing through all radiators at time t
Procedure
Output
  Lower heating efficiency of the boiler [%]
  Upper heating efficiency of the boiler [%]
  Volumetric efficiency of the boiler [J/Nm^3]
Analysis Strategy
May not be sufficient; no access to volumetric flow
Notes: Natural gas from the Groningen field has a lower heating value of 31,65 [MJ/Nm^3] and an upper heating value of 35,17 [MJ/Nm^3] (source: https://nl.wikipedia.org/wiki/Verbrandingswarmte)
The upper heating value includes the potential energy you can fully harvest latent heat present in the exhaust gasses, by letting these condensate within the boiler.
The efficiency percentages you encounter in systems burning natural gas be expresses as upper heating value efficiency of low heating value efficiency. To avoid confusion, make sure you output all metrics below:
When using Groningen natural gas, either calculate:
volumetric efficiency [J/Nm^3] == 31,65 [MJ/Nm^3]  1.000.000 [J/MJ]  lower heating efficiency [%].
volumetric efficiency [J/Nm^3] == 35,17 [MJ/Nm^3]  1.000.000 [J/MJ]  upper heating efficiency [%].

## Slide 36: ?. Calculate boiler efficiency ηupper;CH [%] NOT based on supply and return temperature
Data needed
  <similar data as building model>
Calculation
Output
  Lower heating efficiency of the boiler [%]
  Upper heating efficiency of the boiler [%]
  Volumetric efficiency of the boiler [J/Nm^3]
Analysis Strategy
no good; based on circular reasoning
Notes: Natural gas from the Groningen field has a lower heating value of 31,65 [MJ/Nm^3] and an upper heating value of 35,17 [MJ/Nm^3] (source: https://nl.wikipedia.org/wiki/Verbrandingswarmte)
The upper heating value includes the potential energy you can fully harvest latent heat present in the exhaust gasses, by letting these condensate within the boiler.
The efficiency percentages you encounter in systems burning natural gas be expresses as upper heating value efficiency of low heating value efficiency. To avoid confusion, make sure you output all metrics below:
When using Groningen natural gas, either calculate:
volumetric efficiency [J/Nm^3] == 31,65 [MJ/Nm^3]  1.000.000 [J/MJ]  lower heating efficiency [%].
volumetric efficiency [J/Nm^3] == 35,17 [MJ/Nm^3]  1.000.000 [J/MJ]  upper heating efficiency [%].

## Slide 37: Pre-analysis: Berkum energy pilot
WP3 Data Analysis & Prediction
46 homes/9 blocks ~ 4-6 homes/block; 1 set of interventions/block
Energy saving / heating interventions Aug-17 – Mar-18
  Building: isolation (30y old -> floor + facade + roof + window)
  Installation: heating (gas -> hybrid / full electic (air-air/air-water) heat pump)
  Installation: heating distribution: some with radiator fans
  Installation: ventilation (mechanical -> with heat recovery central/decentral)
Monitoring data May 18 - now
  Available after interventions (+ E+G yearly, several years before)
  BeNext OpenTherm heating control (Tset;Tin;Ts; Tr; CH/DHW)
  BeNext P1 smart meter data (E+, E- [kWh] every second, G+ [kWh] every 5 minutes)
  E+ [W, kWh] heat pump, ventilation (Ecolution)